## E
Alarm list in BSL3 Lab
07/10/2019, 26/02/2020, 03/08/2021, 09/08/2021
Hideki Miki, Ph.D. (Technology), JICA Expert
Note1) Alarm should be divided (classified) for researcher and/ or engineer.
Note2) Alarm panel had better to be installed in each room.
No. | System | Equipment | What occurs? | Frequency? | Detector is ready? | What occurs, as result? | Can control system detect indirectly?
1 | Building system | Wall panel | Seal is Broken. | Approx. 10 years. | No. | Room air leaks. | No.
2 |  | Ceiling panel | Seal is Broken. | Approx. 10 years. | No. | Room air leaks. | No.
3 |  | Floor | Seal is Broken. | Approx. 10 years. | No. | Room air and liquid leak. | No.
4 |  | Window | Seal is Broken. | Approx. 10 years. | No. | Room air leaks. | No.
5 |  | Door | not closed. | Usual by human error. | No. | Room air leaks, and room pressure cannot be controlled. | Yes, by pressure alarm and analyzation. However sensor had better be attached.
6 |  |  | Gasket is damaged. | Approx. 10 years. | No. | Room air leaks. | No.
7 |  |  | Electric lock is broken. | Rare. | No, but detected easily. | Door cannot be opend or closed. | No.
8 | Mechanical system (Air) | Air conditioner | Compressor is broken. | Rare. | Yes. | Room temperature cannot be controlled. | -
9 |  |  | Compressor stops by safety device. | Under defined conditions. | Yes. | Ditto. | -
10 |  |  | Fan belt is broken. | Approx. 8000hrs. | No. | Air volume decreases. Room pressure cannot be controlled. | Yes, by pressure and temperature alarm and analyzation.
11 |  |  | Fan motor is broken. | Rare. | No. | Ditto. | Ditto.
12 |  |  | Fan bearing is broken. | Approx. 20000hrs. | No, but detected easily. | Ditto. | Ditto.
13 |  |  | Coil is clogged. | Rare. | No. | Room temperature and humidity cannot be controlled. | Yes, by temperature and humidity alarm and analyzation.
14 |  | Humidifier | Heater is broken. | Rare. | No. | Room humidity cannot be controlled. | Yes, by humidity alarm and analyzation.
15 |  |  | Spray nozzle is clogged. | Rare. | No. | Ditto. | Ditto.
16 |  | Fan | Belt is broken. | Approx. 8000hrs. | No. | Air volume decreases. Room pressure cannot be controlled. | Yes, by pressure and temperature alarm and analyzation.
17 |  |  | Motor is broken. | Rare. | No. | Ditto. | Ditto.
18 |  |  | Bearing is broken. | Approx. 20000hrs. | No, but detected easily. | Ditto. | No.
19 |  | Filter unit | Rough filter is clogged. | Approx. 3 month in case of supply side. (as designated) | No. | Air volume decreases step by step. Room pressure cannot be controlled step by step. | Yes, by pressure alarm and analyzation.
20 |  |  | Midium efficiency filter is clogged. | Approx. 6 month in case of supply side. (as designated) | No. | Ditto. | Ditto.
21 |  |  | HEPA filter is clogged. | Approx. 1 year in case of supply side. (as designated) | No. | Ditto. | Ditto.
22 |  | MD (Motor Damper) | Actuator is broken. | Rare. | No. | Air volume and room pressure cannot be controlled. | Yes, by pressure alarm and analyzation.
23 |  |  | Sensor is broken. | Rare. | No. | Ditto. | Ditto.
24 |  | CAV (Constant Air Volume) unit | Actuator is broken. | Rare. | No. | Air volume and room pressure cannot be controlled. | Yes, by pressure alarm and analyzation.
25 |  |  | Sensor is broken. | Rare. | No. | Ditto. | Ditto.
26 | Mechanical system (Water) | Waste water treatment unit by heat | Boiler is broken. | Rare. | Yes. | Decontamination cannot be completed. | -
27 |  |  | Control valve is broken. | Rare. | Yes. | Ditto. | -
28 |  |  | Boiler stops by safety device. | Under defined conditions. | Yes. | Ditto. | -
29 |  |  | Temperature sensor is broken. | Rare. | Yes. | Ditto. | -
30 |  |  | Gasket is damaged. | Approx. 3 years. | No. | Air leaks. | -
31 |  | Waste water treatment unit by chemical | Chemical is empty. | Several weeks or months | No. | Decontamination cannot be completed. | -
32 |  |  | Control valve is broken. | Rare. | No. | Ditto. | No.
33 |  |  | Water level sensor is broken. | Rare. | No. | Ditto. | No.
34 |  |  | Chemical concentration sensor is broken or its sensitivity decreases. | Several weeks or months | No. | Ditto. | No.
35 |  | Supply water pump | Motor is broken. | Rare. | No. | Water cannot be sent.
36 |  | Exhaust water pump | Motor is broken. | Rare. | No. | Water cannot be sent.
37 |  | Sink | Over flow | Usual by human error. | No, but detected easily. | Floor is contaminated. | No.
38 |  |  | Water trap is broken. | 1 Month without using. | No. | Air leaks. | No.
39 |  | Hand wash | Over flow | Usual by human error. | No, but detected easily. | Floor is contaminated. | No.
40 |  |  | Water trap is broken. | 1 Month without using. | No. | Air leaks. | No.
41 |  | Shower | Over flow | Usual by human error. | No, but detected easily. | Floor is contaminated. | No.
42 |  |  | Water trap is broken. | 1 Month without using. | No. | Air leaks. | No.
43 | Electric system | [Power source] | Black out | Due to electric company. | No, but detected easily. | All electric devices stop. | No. Also control system stops
44 |  |  | Over or less voltage | Ditto | No. | All electric devices may be broken. | No.
45 |  | Circuit breaker | Over current | Due to electric equipment. | No, but detected easily. | All connected electric devices stop. | No.
46 |  |  | Leakage | Rare. | Yes, in case of ELB. | Ditto. | -
47 |  | Lighting fixture | Lamp is broken except using LED. | Approx. 8000hrs. | No, but detected easily. | Room is dark. | -
48 |  | Generator | Fuel is empty. | Due to fuel capacity. | No. | Emergency electric power cannot be supplied. | No.
49 |  |  | Engine trouble | Rare. | No. | Ditto. | Ditto
50 |  | UPS (Uninterruptible power supply) | Battery is damaged. | Approx. 3year | Yes. | Emergency electric power cannot be supplied. | However alarm is not connected usually.
51 | Experimental system | BSC (Bio Safety Cabinet) | Filter is clogged. | Rare, in case of BSL3 lab. | Yes. | Air volume decreases step by step. | -
52 |  |  | Fan is broken. | Rare. | Yes. | Air volume degreases. | -
53 |  |  | UV lamp is broken. | Approx. 8000hrs. | No. | Decontamination cannot be completed. | No.
54 |  | Autoclave | Boiler is broken. | Rare. | Yes. | Decontamination cannot be completed. | -
55 |  |  | Control valve is broken. | Rare. | Yes. | Ditto. | -
56 |  |  | Boiler stops by safety device. | Under defined conditions. | Yes. | Ditto. | -
57 |  |  | Gasket is damaged. | Approx. 3 years. | No. | Air leaks, and decontamination cannot be completed. | -
58 |  | Pass box | UV lamp is broken. | Approx. 8000hrs. | No. | Decontamination cannot be completed. | No.
59 |  |  | Gasket is damaged. | Approx. 3 years. | No. | Air leaks. | -
60 |  | Dunk tank | Over flow | Usual by human error. | No. | Floor is contaminated. | No.
61 |  |  | Chemical is empty. | Rare. | Yes. | Decontamination cannot be completed. | -
62 |  | Freezer | Compressor is broken. | Rare. | No. | Inside temperature cannot be controlled, and sample is lost. | No.
63 |  |  | Compressor stops by safety device. | Under defined conditions. | No. | Ditto. | No.
64 |  | Incubator | Broken. | Rare. | No. | Inside temperature cannot be controlled, and sample is lost. | No.
65 | Security system | Door lock | Broken. | Rare. | No, but detected easily. | In and out is impossible. | No.
66 |  | Card reader | Broken. | Rare. | No, but detected easily. | In and out is impossible. | No.
67 |  | Monitoring camera | Broken. | Rare. | No, but detected easily. | Target area cannot be visible. | No.
68 |  | Speaker | Broken. | Rare. | No, but detected easily. | Target area cannot be communicated. | No.
69 |  | Telephone | Broken. | Rare. | No, but detected easily. | Target area cannot be communicated. | No.
70 |  | Fire detector | Broken. | Rare. | No. | Fire cannot be detected. | No.
71 | Control system | PLC (Programable Logic Controller) | Battery is empty, exept using capaciter. | Arround 3 years. | No. | Program is lost in case of black out. | No.
72 |  | Personal computer | Broken. | Rare. | No, but detected easily. | Operation condition cannot be visible. | No.
73 |  | Recorder | Chart paper is empty in case of using paper and ink. | Several weeks or months. | No, but detected easily. | Operation condition cannot be recorded. | No.
74 |  |  | Ink is empty in case of using paper and ink. | Ditto. | Ditto. | Ditto. | No.
75 |  |  | Broken. | Rare. | No. | Ditto. | No.
76 |  | Pressure sensor | Broken. | Rare. | No, but detected easily. | Room pressure cannot be controlled. | No.
77 |  | Temperature sensor | Broken. | Rare. | No, but detected easily. | Temperature cannot be controlled. | No.
78 |  | Humidity sensor | Broken. | Rare. | No, but detected easily. | Humidity cannot be controlled. | No.
79 |  | Power source | Electrolytic capacitor is broken. | Approx. 10 years. | No, but detected easily. | Power failure. | No.
80 | Others

## J
BSL3実験室における警報リスト
07/10/2019, 26/02/2020, 03/08/2021, 09/08/2021
Hideki Miki, Ph.D. (Technology), JICA Expert
注1）アラームは、研究者および/またはエンジニアのために分割（分類）する必要がある。
注2）警報パネルは各部屋に設置されたほうがよい。
No. | システム | 機器 | 何が起こるか? | 頻度は? | 検知器はあるか? | 結果として、何が起こるか? | 制御システムは間接的に検知できるか?
1 | 建築システム | 壁パネル | シールが切れる。 | 約10年。 | いいえ。 | 室内空気が漏れる。 | いいえ。
2 |  | 天井パネル | シールが切れる。 | 約10年。 | いいえ。 | 室内空気が漏れる。 | いいえ。
3 |  | 床 | シールが切れる。 | 約10年。 | いいえ。 | 室内空気と液体が漏れる。 | いいえ。
4 |  | 窓 | シールが切れる。 | 約10年。 | いいえ。 | 室内空気が漏れる。 | いいえ。
5 |  | 扉 | 閉まらない。 | ヒューマンエラーによって通常に。 | いいえ。 | 室内空気が漏れて、室内圧力が制御できない。 | はい、圧力警報と分析によって。ただしセンサーが設置されるほうがよい。
6 |  |  | ガスケットが傷む。 | 約10年。 | いいえ。 | 室内空気が漏れる。 | いいえ。
7 |  |  | 電気錠が壊れる。 | まれ。 | いいえ、しかし検知は容易。 | 扉を開けられない、または閉められない。 | いいえ。
8 | 機械システム (空気) | 空調機 | 圧縮機が壊れる。 | まれ。 | はい。 | 室内温度が制御できない。 | -
9 |  |  | 安全装置によって圧縮機が停まる。 | 規定の条件下で。 | はい。 | 同上。 | -
10 |  |  | ファンベルトが切れる。 | 約8000時間。 | いいえ。 | 風量が減って、室内圧力が制御できない。 | はい、圧力警報、温度警報と分析によって。
11 |  |  | ファンモーターが壊れる。 | まれ。 | いいえ。 | 同上。 | 同上。
12 |  |  | ファンベアリングが壊れる。 | 約20000時間。 | いいえ、しかし検知は容易。 | 同上。 | 同上。
13 |  |  | コイルが詰まる。 | まれ。 | いいえ。 | 室内温湿度が制御できない。 | はい、温湿度警報と分析によって。
14 |  | 加湿器 | ヒーターが壊れる。 | まれ。 | いいえ。 | 室内湿度が制御できない。 | はい、湿度警報と分析によって。
15 |  |  | スプレーノズルが詰まる。 | まれ。 | いいえ。 | 同上。 | 同上。
16 |  | ファン | ベルトが切れる。 | 約8000時間。 | いいえ。 | 風量が減って、室内圧力が制御できない。 | はい、圧力警報、温度警報と分析によって。
17 |  |  | モーターが壊れる。 | まれ。 | いいえ。 | 同上。 | 同上。
18 |  |  | ベアリングが壊れる。 | 約20000時間。 | いいえ、しかし検知は容易。 | 同上。 | 同上。
19 |  | フィルターユニット | 粗塵フィルターが詰まる。 | 給気側の場合、約3ヶ月 (設計通り)。 | いいえ。 | 風量が徐々に減って、室内圧力が徐々に制御できない。 | はい、圧力警報と分析によって。
20 |  |  | 中性能フィルターが詰まる。 | 給気側の場合、約6ヶ月 (設計通り)。 | 同上。 | 同上。 | 同上。
21 |  |  | HEPAフィルターが詰まる。 | 給気側の場合、約1年 (設計通り)。 | 同上。 | 同上。 | 同上。
22 |  | モーターダンパー (MD) | 動作器 が壊れる。 | まれ。 | いいえ。 | 風量と室内圧力が制御できない。 | はい、圧力警報と分析によって。
23 |  |  | センサーが壊れる。 | まれ。 | いいえ。 | 同上。 | 同上。
24 |  | 定風量装置 (CAV) | 動作器 が壊れる。 | まれ。 | いいえ。 | 風量と室内圧力が制御できない。 | はい、圧力警報と分析によって。
25 |  |  | センサーが壊れる。 | まれ。 | いいえ。 | 同上。 | 同上。
26 | 機械システム (水) | 加熱式排水処理装置 | ボイラーが壊れる。 | まれ。 | はい。 | 滅菌ができない。 | -
27 |  |  | 制御弁が壊れる。 | まれ。 | はい。 | 同上。 | -
28 |  |  | 安全装置によってボイラーが停まる。 | 規定の条件下で。 | はい。 | 同上。 | -
29 |  |  | 温度センサーが壊れる。 | まれ。 | はい。 | 同上。 | -
30 |  |  | ガスケットが傷む。 | 約10年。 | いいえ。 | 空気が漏れる。 | いいえ。
31 |  | 薬液式排水処理装置 | 薬液が切れる。 | 数週間または数ヶ月。 | はい。 | 滅菌ができない。 | -
32 |  |  | 制御弁が壊れる。 | まれ。 | いいえ。 | 同上。 | いいえ。
33 |  |  | 水位センサーが壊れる。 | まれ。 | いいえ。 | 同上。 | いいえ。
34 |  |  | 薬液濃度センサーが壊れる、または感度が低下する。 | 数週間または数ヶ月。 | いいえ。 | 同上。 | いいえ。
35 |  | 給水ポンプ | モーターが壊れる。 | まれ。 | いいえ。 | 水を送れない。 | いいえ。
36 |  | 排水ポンプ | モーターが壊れる。 | まれ。 | いいえ。 | 同上。 | いいえ。
37 |  | 流し | 水が溢れる。 | ヒューマンエラーによって通常に。 | いいえ、しかし検知は容易。 | 床が汚れる。 | いいえ。
38 |  |  | 封水が破れる。 | 使わなければ1ヶ月。 | いいえ。 | 空気が漏れる。 | いいえ。
39 |  | 手洗い器 | 水が溢れる。 | ヒューマンエラーによって通常に。 | いいえ、しかし検知は容易。 | 床が汚れる。 | いいえ。
40 |  |  | 封水が破れる。 | 使わなければ1ヶ月。 | いいえ。 | 空気が漏れる。 | いいえ。
41 |  | シャワー | 水が溢れる。 | ヒューマンエラーによって通常に。 | いいえ、しかし検知は容易。 | 床が汚れる。 | いいえ。
42 |  |  | 封水が破れる。 | 使わなければ1ヶ月。 | いいえ。 | 空気が漏れる。 | いいえ。
43 | 電気システム | [電源] | 停電。 | 電力会社による。 | いいえ、しかし検知は容易。 | 全ての電機機器が停まる。 | いいえ、同じく制御システムも停まる。
44 |  |  | 電圧が高い、または低い。 | 同上。 | いいえ。 | 全ての電機機器が壊れるおそれがある。 | いいえ。
45 |  | サーキットブレーカー | 過電流。 | 電気機器による。 | いいえ、しかし検知は容易。 | 全ての接続された電気機器が停まる。 | いいえ。
46 |  |  | 漏電。 | まれ。 | はい、ELBの場合。 | 同上。 | -
47 |  | 照明器具 | LEDを使わない場合、ランプが切れる。. | 約8000時間。 | いいえ、しかし検知は容易。 | 室内が暗い。 | -
48 |  | 発電機 | 燃料が切れる。 | 燃料容量による。 | いいえ。 | 非常用電源が供給されない。 | いいえ。
49 |  |  | エンジン故障。 | まれ。 | いいえ。 | 同上。 | 同上。
50 |  | 無停電装置 (UPS) | バッテリーが傷む。 | 約3年。 | はい。 | 非常用電源が供給されない。 | ただし警報は通常、接続されない。
51 | 実験システム | 安全キャビネット (BSC) | フィルターが詰まる。 | BSL3実験室の場合、まれ。 | はい。 | 風量が徐々に減る。 | -
52 |  |  | ファンが壊れる。 | まれ。 | はい。 | 風量が減る。 | -
53 |  |  | UVランプが切れる。 | 約8000時間。 | いいえ。 | 滅菌ができない。 | いいえ。
54 |  | オートクレーブ | ボイラーが壊れる。 | まれ。 | はい。 | 滅菌ができない。 | -
55 |  |  | 制御弁が壊れる。 | まれ。 | はい。 | 同上。 | -
56 |  |  | 安全装置によってボイラーが停まる。 | 規定の条件下で。 | はい。 | 同上。 | -
57 |  |  | ガスケットが傷む。 | 約3年。 | いいえ。 | 空気が漏れて、滅菌ができない。 | -
58 |  | パスボックス | UVランプが切れる。 | 約8000時間。 | いいえ。 | 滅菌ができない。 | いいえ。
59 |  |  | ガスケットが傷む。 | 約3年。 | いいえ。 | 空気が漏れる。 | -
60 |  | ダンクタンク | 水が溢れる。 | ヒューマンエラーによって通常に。 | いいえ。 | 床が汚れる。 | いいえ。
61 |  |  | 薬液が切れる。 | 数週間または数ヶ月。 | はい。 | 滅菌ができない。 | いいえ。
62 |  | フリーザー | 圧縮機が壊れる。 | まれ。 | いいえ。 | 内部温度が制御できず、標本が失われる。 | いいえ。
63 |  |  | 安全装置によって圧縮機が停まる。 | 規定の条件下で。 | いいえ。 | 同上。 | いいえ。
64 |  | インキュベーター | 壊れる。 | まれ。 | いいえ。 | 内部温度が制御できず、標本が失われる。 | いいえ。
65 | 保安システム | ドアロック | 壊れる。 | まれ。 | いいえ、しかし検知は容易。 | 出入りができない。 | いいえ。
66 |  | カードリーダー | 壊れる。 | まれ。 | いいえ、しかし検知は容易。 | 出入りができない。 | いいえ。
67 |  | 監視カメラ | 壊れる。 | まれ。 | いいえ、しかし検知は容易。 | 対象範囲が見えない。 | いいえ。
68 |  | スピーカー | 壊れる。 | まれ。 | いいえ、しかし検知は容易。 | 対象範囲が連絡できない。 | いいえ。
69 |  | 電話 | 壊れる。 | まれ。 | いいえ、しかし検知は容易。 | 対象範囲が連絡できない。 | いいえ。
70 |  | 火災検知器 | 壊れる。 | まれ。 | いいえ。 | 火事が検知できない。 | いいえ。
71 | 制御システム | プログラマブルロジックコントローラー (PLC) | キャパシタを使わない場合、バッテリーが切れる。 | 約3年。 | いいえ。 | 停電の場合、プログラムが消える。 | いいえ。
72 |  | パーソナルコンピューター | 壊れる。 | まれ。 | いいえ、しかし検知は容易。 | 運転状態が見えない。 | いいえ。
73 |  | 記録計 | 記録紙とインクを使う場合、記録紙が切れる。 | 数週間または数ヶ月。 | いいえ、しかし検知は容易。 | 運転状態が記録できない。 | いいえ。
74 |  |  | 記録紙とインクを使う場合、インクが切れる。 | 同上。 | 同上。 | 同上。 | いいえ。
75 |  |  | 壊れる。 | まれ。 | いいえ。 | 同上。 | いいえ。
76 |  | 圧力センサー | 壊れる。 | まれ。 | いいえ、しかし検知は容易。 | 圧力が制御できない。 | いいえ。
77 |  | 温度センサー | 壊れる。 | まれ。 | いいえ、しかし検知は容易。 | 温度が制御できない。 | いいえ。
78 |  | 湿度センサー | 壊れる。 | まれ。 | いいえ、しかし検知は容易。 | 湿度が制御できない。 | いいえ。
79 |  | 電源 | 電解コンデンサが壊れる。 | 約10年。 | いいえ、しかし検知は容易。 | 停電。 | いいえ。
80 | その他