## Input form
Form8 Record of dairy checking BSL-3 Mobile Laboratory
Re-start date |  | 2007-07-10
Mesuring time : |  | 9:00～9:30 in principle
Person : |  | Mr.xxxx, Ms.xxxx
Table1 The change of Filter pressure loss, Open/close ratio of room pressure control dumper, Room pressure.
| (note) |  | PFU includes rough and middle efficincy filter, SFU and EFU include HEPA filter.
| (note) |  | Passage days is counted from Re-start date, in the day filter were changed.
Date | Passage days [days] | weather | temperature |  | humidity |  | Filter pressure loss[Pa] | [6 empty] | Open/close ratio of room pressure control dumper [%] |  | Room pressure [Pa] |  | Remark (sound, vibration, smell, getting wet, etc)
[7 empty] | Supply air side |  |  |  | Exthost air side
|  |  | outside | L. room | outside | L. room | PFU | SFU1-1 | SFU1-2 | SFU2 | EFU2 | EFU3 | EFU1 | L. room | A.room | L. room | A.room
2007-07-10 | 0 | hot | 31.8 | 27.3 |  | 41.1 | 22 | 120 | 105 | 65 | 65 | 60 | 70 | 17 | 29 | -69 | -34
2007-07-11 | 1 | Sunny, little cloudy | 34.3 | 28.4 |  | 36.9 | 22 | 120 | 110 | 65 | 65 | 60 | 75 | 20 | 59 | -71 | -26
2007-07-12 | 2 | Sunny, little cloudy | 34.9 | 28.8 |  | 39.7 | 26 | 125 | 20 | 65 | 115 | 65 | 70 | 17 | 100 | -71 | -14
2007-07-13 | 3 | hot | 35.7 | 28.6 |  | 41.6 | 26 | 110 | 120 | 65 | 65 | 60 | 65 | 20 | 46 | -66 | -35
2007-07-14 | 4
2007-07-15 | 5
2007-07-16 | 6
2007-07-17 | 7
2007-07-18 | 8
2007-07-19 | 9
2007-07-20 | 10 | cloudy | 34.6 | 27.7 |  | 43.6 | 28 | 120 | 120 | 62 | 65 | 60 | 70 | 22 | 47 | -71 | -33
2007-07-21 | 11
2007-07-22 | 12
2007-07-23 | 13 | rain in afternoon | 36.3 | 27.8 |  | 40.2 | 28 | 120 | 118 | 65 | 65 | 60 | 70 | 25 | 50 | -68 | -29
2007-07-24 | 14 | rain in afternoon | 36.9 | 28.1 |  | 43.1 | 28 | 120 | 115 | 65 | 65 | 60 | 70 | 30 | 55 | -68 | -30
2007-07-25 | 15 | cool all day | 32 | 26.8 |  | 43.1 | 28 | 125 | 115 | 65 | 65 | 60 | 70 | 21 | 57 | -67 | -26
2007-07-26 | 16 | Sunny | 31.9 | 27 |  | 46.6 | 30 | 120 | 118 | 65 | 65 | 60 | 68 | 30 | 49 | -70 | -30
2007-07-27 | 17 | rain in morning | 28.6 | 26.5 |  | 56.5 | 30 | 125 | 120 | 65 | 65 | 60 | 70 | 13 | 55 | -69 | -29 | no abnormality.
2007-07-28 | 18
2007-07-29 | 19
2007-07-30 | 20 | hot | 33.1 | 27.4 |  | 41.2 | 30 | 120 | 118 | 65 | 65 | 60 | 70 | 25 | 46 | -69 | -30
2007-07-31 | 21 | hot | 31.8 | 27.2 |  | 48.6 | 30 | 120 | 118 | 65 | 65 | 60 | 68 | 16 | 58 | -70 | -27
2007-08-01 | 22 | hot | 31.8 | 26.8 |  | 48.7 | 28 | 122 | 120 | 65 | 65 | 60 | 66 | 11 | 53 | -71 | -28
2007-08-02 | 23 | cloudy | 30.1 | 26.3 |  | 52.9 | 28 | 125 | 120 | 65 | 65 | 60 | 68 | 12 | 59 | -68 | -25
2007-08-03 | 24 | Sunny | 34.3 | 27 |  | 46.9 | 30 | 122 | 118 | 65 | 65 | 60 | 65 | 23 | 52 | -66 | -28
2007-08-04 | 25
2007-08-05 | 26
2007-08-06 | 27 | cloudy | 30.8 | 27.5 |  | 53.2 | 30 | 122 | 120 | 65 | 65 | 60 | 70 | 26 | 62 | -70 | -23
2007-08-07 | 28 | liltle cloudy | 31.5 | 26.6 |  | 44.3 | 30 | 122 | 120 | 65 | 65 | 60 | 68 | 28 | 55 | -70 | -28
2007-08-08 | 29 | liltle cloudy | 31.4 | 26.8 |  | 43.6 | 30 | 122 | 120 | 65 | 65 | 60 | 68 | 14 | 49 | -71 | -33
2007-08-09 | 30 | hot | 32.5 | 27.4 |  | 42.4 | 30 | 120 | 118 | 65 | 65 | 60 | 70 | 27 | 58 | -69 | -31
2007-08-10 | 31 | rain | 29.1 | 26.9 |  | 61.6 | 30 | 125 | 120 | 65 | 65 | 60 | 60 | 22 | 53 | -68 | -27
2007-08-11 | 32
2007-08-12 | 33
2007-08-13 | 34 | hot | 33.2 | 27.4 |  | 44.5 | 30 | 120 | 115 | 65 | 65 | 60 | 62 | 11 | 61 | -69 | -24
2007-08-14 | 35 | cloudy | 30.9 | 27.1 |  | 48.6 | 30 | 122 | 118 | 65 | 65 | 60 | 60 | 21 | 50 | -72 | -29
2007-08-15 | 36 | cloudy | 30.4 | 27.5 |  | 56 | 30 | 122 | 120 | 65 | 65 | 60 | 65 | 26 | 58 | -68 | -27
2007-08-16 | 37 | cloudy | 31.7 | 27.5 |  | 43.3 | 30 | 122 | 118 | 65 | 65 | 60 | 65 | 27 | 51 | -68 | -29
2007-08-17 | 38 | cloudy | 30 | 27 |  | 51.2 | 30 | 120 | 118 | 65 | 65 | 60 | 65 | 25 | 55 | -68 | -28
2007-08-18 | 39
2007-08-19 | 40
2007-08-20 | 41 | rain in moorning | 32.5 | 27.3 |  | 43.5 | 30 | 120 | 116 | 65 | 65 | 60 | 65 | 18 | 55 | -70 | -31 | 16h45 decrease the set temperature of PAC form 25 to 23 because to hot
2007-08-21 | 42 | rain in afternoon | 33.2 | 26.4 |  | 44.6 | 30 | 122 | 120 | 65 | 65 | 60 | 65 | 28 | 63 | -69 | -27 | no abnormality.
2007-08-22 | 43 | cool all day | 28.5 | 25.2 |  | 43.1 | 30 | 120 | 118 | 65 | 65 | 60 | 65 | 15 | 57 | -67 | -29 | the recorder stop 10 hours, the reason is loss of power
2007-08-23 | 44 | cool all day | 31.4 | 26 |  | 44.3 | 30 | 122 | 118 | 65 | 65 | 60 | 62 | 24 | 54 | -70 | -33 | increase the set temperature of PAC form 23 to 24
2007-08-24 | 45 | cool all day | 28.9 | 26.2 |  | 51.8 | 30 | 122 | 120 | 65 | 65 | 60 | 62 | 23 | 51 | -72 | -31 | no abnormality.
2007-08-25 | 46 | [16 empty] | Stop the mobilab at 11h20 to repair the electric system of NIHE, 12h20 run the mobilab
2007-08-26 | 47 | [16 empty] | no abnormality.
2007-08-27 | 48 | cool all day,cloudy | 28.8 | 25.8 |  | 50.8 | 30 | 125 | 118 | 62 | 65 | 60 | 60 | 21 | 59 | -69 | -29 | no abnormality.
2007-08-28 | 49 | cool all day,cloudy | 30.7 | 26.1 |  | 47.1 | 30 | 122 | 120 | 65 | 65 | 60 | 62 | 11 | 45 | -70 | -33 | no abnormality.
2007-08-29 | 50 | rain | 27.6 | 26 |  | 64.3 | 30 | 130 | 125 | 65 | 65 | 60 | 60 | 26 | 64 | -65 | -29 | cleanup 2 supply air filter, by ITAGAKI sensei and Dung
2007-08-30 | 51 | cool all day | 30.6 | 26.9 |  | 44.4 | 30 | 125 | 120 | 65 | 65 | 60 | 62 | 23 | 50 | -70 | -35 | no abnormality.
2007-08-31 | 52 | cool all day | 30 | 25.9 |  | 51.6 | 30 | 125 | 122 | 65 | 65 | 60 | 62 | 25 | 65 | -70 | -29 | no abnormality.
2007-09-01 | 53 | [16 empty] | no abnormality.
2007-09-02 | 54 | [16 empty] | no abnormality.
2007-09-03 | 55 | [16 empty] | no abnormality.
2007-09-04 | 56 | rain | 29.7 | 26 |  | 52.9 | 30 | 130 | 128 | 70 | 65 | 60 | 60 | 16 | 58 | -73 | -31 | change the ink for the recorder.
2007-09-05 | 57 | rain | 25.9 | 26.6 |  | 52.8 | 30 | 130 | 130 | 65 | 65 | 60 | 60 | 22 | 55 | -70 | -30 | no abnormality.
2007-09-06 | 58 | cool | 28.3 | 25.6 |  | 44 | 30 | 125 | 120 | 65 | 65 | 60 | 60 | 17 | 48 | -68 | -32 | no abnormality.
2007-09-07 | 59 | cool | 30.8 | 25.6 |  | 47.2 | 30 | 125 | 120 | 65 | 60 | 60 | 60 | 20 | 62 | -69 | -33 | no abnormality.
2007-09-08 | 60 | [16 empty] | no abnormality.
2007-09-09 | 61 | [16 empty] | no abnormality.
2007-09-10 | 62 | cool | 25.8 | 25.1 |  | 48.3 | 30 | 130 | 120 | 70 | 65 | 60 | 60 | 18 | 56 | -67 | -27 | no abnormality.
2007-09-11 | 63 | cloudy | 28.4 | 26.1 |  | 44.2 | 35 | 125 | 120 | 65 | 65 | 60 | 60 | 23 | 48 | -69 | -26 | change the set valua of PAC from 24 to 25
2007-09-12 | 64 | cloudy | 28.6 | 26.2 |  | 58.8 | 30 | 130 | 125 | 65 | 65 | 60 | 55 | 9 | 55 | -66 | -34 | decrease the set valua of PAC from 25 to 24
2007-09-13 | 65 | rain | 30.6 | 26.1 |  | 57.3 | 30 | 125 | 125 | 65 | 65 | 60 | 60 | 10 | 51 | -70 | -31 | no abnormality.
2007-09-14 | 66 | hot | 26.5 | 25.6 |  | 47.2 | 32 | 130 | 120 | 65 | 60 | 60 | 60 | 9 | 60 | -70 | -33 | EF1 has the unusual voice
2007-09-15 | 67 | [16 empty] | no abnormality.
2007-09-16 | 68 | [16 empty] | no abnormality.
2007-09-17 | 69 | rain | 26 | 26.6 |  | 52.1 | 30 | 130 | 120 | 70 | 65 | 60 | 60 | 23 | 74 | -69 | -27 | no abnormality.
2007-09-18 | 70 | rain | 26 | 26.6 |  | 52.1 | 30 | 135 | 130 | 70 | 65 | 60 | 60 | 20 | 80 | -69 | -27 | Ante Room has unusual water (the reason is the heavy rain last night)
2007-09-19 | 71 | cloudy | 30.4 | 26.3 |  | 43.4 | 35 | 130 | 120 | 65 | 60 | 60 | 62 | 20 | 76 | -68 | -29 | no abnormality.
2007-09-20 | 72 | rain | 29.6 | 26.9 | 42 | 40.9 | 32 | 125 | 120 | 65 | 65 | 60 | 65 | 23 | 75 | -70 | -29 | no abnormality.
2007-09-21 | 73 | rain | 26.8 | 30.3 | 40 | 37.1 | 32 | 125 | 120 | 65 | 65 | 60 | 60 | 21 | 75 | -71 | -29 | no abnormality.
2007-09-22 | 74 | [16 empty] | no abnormality.
2007-09-23 | 75 | [16 empty] | no abnormality.
2007-09-24 | 76 | cloudy | 30.6 | 27.1 | 40 | 40.5 | 35 | 125 | 115 | 65 | 60 | 60 | 55 | 30 | 67 | -72 | -31 | degrease the set temperature from 24 to 23 by Dung and Hang
2007-09-25 | 77 | rain | 25.5 | 27 | 70 | 53.4 | 33 | 135 | 130 | 70 | 70 | 60 | 55 | 34 | 69 | -70 | -35 | no abnormality.
2007-09-26 | 78 | rain | 26.5 | 26.6 | 65 | 56.4 | 35 | 140 | 140 | 70 | 60 | 60 | 55 | 20 | 80 | -63 | -28 | no abnormality.
2007-09-27 | 79 | rain | 26.1 | 26.6 | 72 | 54.3 | 33 | 135 | 128 | 65 | 65 | 60 | 50 | 32 | 79 | -70 | -34 | no abnormality.
2007-09-28 | 80 | rain in morning | 29.6 | 25.1 | 58 | 45.6 | 35 | 130 | 120 | 65 | 65 | 60 | 55 | 30 | 66 | -67 | -35 | Miki changed set value of L.room pressure from 70 to 60.
2007-09-29 | 81 | [16 empty] | no abnormality.
2007-09-30 | 82 | [16 empty] | no abnormality.
2007-10-01 | 83 | sunny | 32.6 | 26.7 | 40 | 36.6 | 35 | 125 | 120 | 65 | 65 | 60 | 50 |  |  | -56 | -28 | EF1 had sound, it had water around PAC. Increase the set pessure of Lab from -70 to -60
2007-10-02 | 84 | sunny | 30.2 | 24.9 | 52 | 44.1 | 35 | 125 | 120 | 70 | 65 | 60 | 50 |  |  | -60 | -27 | no abnormality.
2007-10-03 | 85 | rain | 27.3 | 26.5 | 70 | 47.3 | 35 | 135 | 120 | 70 | 65 | 60 | 50 | 25 | 65 | -59 | -30 | water from outside thought to machine room, pasted silicon by Itagaki sensei and Dung
2007-10-04 | 86 | rain | 26 | 27 | 75 | 45.4 | 35 | 135 | 120 | 70 | 65 | 60 | 45 | 38 | 65 | -59 | -26 | water from outside thought to machine room, pasted silicon by Itagaki sensei and Hang
2007-10-05 | 87 | rain | 24.3 | 26.5 | 76 | 52.5 | 35 | 140 | 135 | 75 | 60 | 60 | 40 | 11 | 65 | -64 | -30 | same 10/4
2007-10-06 | 88
2007-10-07 | 89
2007-10-08 | 90 | cloudy | 29.1 | 25.4 | 66 | 44.4 | 35 | 130 | 125 | 65 | 65 | 60 | 45 | 37 | 70 | -58 | -31 | there was strange sound in fan system; Itagaki Sensei and Dzung paste silicon on the wall of machine room.
2007-10-09 | 91 | sunny | 30.2 | 28.6 | 44 | 35.4 | 38 | 125 | 120 | 70 | 70 | 60 | 52 | 46 | 75 | -59 | -32 | Miki sensei and Hang, Dzung check supply air volume
2007-10-10 | 92 | rainy | 27.9 | 27.4 | 62 | 46.6 | 38 | 135 | 130 | 65 | 65 | 60 | 50 | 37 | 65 | -57 | -26
2007-10-11 | 93 | [16 empty] | Lab. Room temperature was high
2007-10-12 | 94 | cloudy | 27.7 | 28 | 58 | 43 | 38 | 140 | 130 | 65 | 65 | 60 | 45 | 20 | 72 | -65 | -30 | Lab. Room temperature was high
2007-10-13 | 95
2007-10-14 | 96
2007-10-15 | 97 | Sunny | 26 | 27.4 | 55 | 48.6 | 35 | 140 | 130 | 70 | 65 | 60 | 45 | 30 | 62 | -60 | -32 | Lab. Room temperature was high, had strange sound in fan and PAC
2007-10-16 | 98 | cloudy | 24.5 | 26 | 52 | 48 | 35 | 135 | 125 | 70 | 65 | 60 | 50 | 44 | 77 | -62 | -24 | Lab. Room temperature was high, had strange sound in fan and PAC
2007-10-17 | 99 | sunny | 26.1 | 27.7 | 45 | 43.7 | 35 | 135 | 125 | 70 | 65 | 60 | 50 | 25 | 69 | -58 | -30 | Lab. Room temperature was high, had strange sound in fan and PAC
2007-10-18 | 100 | sunny | 25.9 | 29.2 | 50 | 43.8 | 35 | 135 | 125 | 70 | 65 | 60 | 45 | 35 | 70 | -60 | -27 | Lab. Room temperature was high.
2007-10-19 | 101 | sunny | 27.7 | 28.1 | 42 | 44.8 | 40 | 135 | 125 | 65 | 65 | 60 | 55 | 45 | 64 | -58 | -33 | Lab. Room temperature was high.
2007-10-20 | 102
2007-10-21 | 103
2007-10-22 | 104 | sunny | 25.2 | 27.7 | 60 | 47.1 | 40 | 140 | 135 | 70 | 65 | 60 | 45 | 25 | 79 | -59 | -31 | there is sound at upper of PFU0 and fan of PAC hot block
2007-10-23 | 105 | sunny | 26.1 | 28.8 | 60 | 49 | 40 | 140 | 135 | 70 | 65 | 60 | 40 | 9 | 70 | -60 | -32 | Mr. Dzung repairs the sound at upper of PFU0
2007-10-24 | 106 | sunny | 27.4 | 29.4 | 55 | 41.4 | 40 | 140 | 135 | 70 | 65 | 60 | 38 | 12 | 60 | -60 | -27 | Decrease PAC set point temperature to 21
2007-10-25 | 107 | [16 empty] | Increase PAC set point temperature to 25
2007-10-26 | 108 | sunny | 25.9 | 28.9 | 60 | 45.9 | 40 | 145 | 140 | 70 | 65 | 60 | 38 | 7 | 71 | -60 | -30
2007-10-27 | 109
2007-10-28 | 110
2007-10-29 | 111 | sunny | 27.4 | 30.3 | 52 | 39.3 | 45 | 140 | 135 | 70 | 65 | 60 | 35 | 20 | 63 | -65 | -29 | Metec Comp. check Outside Unit (AHU) and spray water to wash filter; Mr.Itagaki and Ms.Hang measured temp. of Lab : about 24-25 degree.
2007-10-30 | 112 | sunny | 25.4 | 28.5 | 55 | 49.8 | 45 | 145 | 135 | 70 | 65 | 60 | 35 | 8 | 62 | -59 | -25 | PUHV-P224M-E has sounded creakly
2007-10-31 | 113 | rainy | 20.8 | 28.3 | 75 | 52.4 | 45 | 130 | 125 | 70 | 65 | 60 | 45 | 22 | 71 | -62 | -34
2007-11-01 | 114 | rainy | 21 | 28.6 | 77 | 50 | 45 | 130 | 125 | 70 | 65 | 60 | 45 | 40 | 69 | -62 | -29 | Reseachers said that it was very hot in Lab. -> Ms. Hang measured temp. of Lab 26.4 degree
2007-11-02 | 115 | cloudy | 20.9 | 28.6 | 51 | 38 | 45 | 125 | 120 | 70 | 65 | 60 | 50 | 29 | 79 | -60 | -24
2007-11-03 | 116 | sunny
2007-11-04 | 117 | sunny
2007-11-05 | 118 | sunny | 21.5 | 29.4 | 40 | 34.2 | 50 | 125 | 115 | 75 | 65 | 60 | 50 | 23 | 72 | -62 | -28 | There is sound because screw was loose. Screw was tighten.
2007-11-06 | 119 | sunny | 21.8 | 29.1 | 58 | 40.9 | 50 | 125 | 120 | 70 | 60 | 60 | 45 | 36 | 66 | -62 | -24
2007-11-07 | 120 | sunny | 23 | 31.6 | 50 | 37.8 | 50 | 125 | 120 | 75 | 65 | 60 | 40 | 21 | 78 | -60 | -33
2007-11-08 | 121 | sunny | 24.7 | 32.9 | 40 | 30.9 | 50 | 125 | 120 | 75 | 65 | 60 | 45 | 22 | 89 | -62 | -33 | Metec Comp. check gas leakage but measurement equipment was not suitable with gas valve of PAC; Changed curoa line of PAC.Temp. set point for PAC 22 degree, measured Lab. temp. was 20 degree.
2007-11-09 | 122 | sunny | 23.2 | 28.7 | 55 | 42.7 | 55 | 130 | 120 | 75 | 60 | 60 | 45 | 26 | 81 | -56 | -29 | Temp. set point for PAC 25 degree, measured Lab. Temp. was 24 degree.
2007-11-10 | 123
2007-11-11 | 124
2007-11-12 | 125 | sunny | 29.2 | 26.3 |  |  | 60 | 145 | 135 | 80 | 68 | 60 | 30 | 14 | 70 | -58 | -28
2007-11-13 | 126 | sunny | 28.8 | 25.6 |  |  | 60 | 148 | 140 | 80 | 70 | 60 | 30 | 4 | 63 | -63 | -28
2007-11-14 | 127 | sunny | 25.4 | 29.1 | 55 | 41.6 | 65 | 145 | 135 | 75 | 65 | 60 | 30 | 4 | 66 | -63 | -31 | check temperature of Lab. Room: 23 degree
2007-11-15 | 128 | sunny | 26.4 | 26.8 | 45 | 37.5 | 75 | 165 | 155 | 75 | 65 | 60 | 55 | 45 | 65 | -58 | -27 | Mr.Itagaki and Ms. Hang shut SA valve: 50%
2007-11-16 | 129 | sunny | 24.5 | 26.1 | 55 | 39.8 | 75 | 155 | 155 | 75 | 65 | 60 | 55 | 28 | 69 | -62 | -31 | Changed Pre-Filter
2007-11-17 | 130
2007-11-18 | 131
2007-11-19 | 132 | sunny | 23.3 | 26.7 |  | 36.8 | 22 | 140 | 135 | 75 | 70 | 60 | 60 | 34 | 61 | -65 | -25 | normal
2007-11-20 | 133 | sunny | 24.1 | 28.2 |  | 39.4 | 22 | 140 | 135 | 75 | 65 | 60 | 55 | 44 | 61 | -53 | -31 | Electric stopped 2 times from 23-24h; Room Pressure alarmed
2007-11-21 | 134 | sunny | 24.3 | 28.9 |  | 38.7 | 22 | 145 | 135 | 75 | 68 | 60 | 55 | 48 | 71 | -57 | -25 | normal
2007-11-22 | 135 | sunny | 23.2 | 28.4 |  | 42.9 | 25 | 145 | 140 | 75 | 70 | 60 | 55 | 26 | 75 | -60 | -29 | normal
2007-11-23 | 136 | sunny | 24.7 | 28.8 |  | 42.9 | 25 | 150 | 145 | 80 | 68 | 60 | 50 | 46 | 75 | -54 | -27 | normal
2007-11-24 | 137
2007-11-25 | 138
2007-11-26 | 139 | sunny | 26.1 | 28.5 |  | 32.7 | 30 | 145 | 140 | 78 | 70 | 60 | 50 | 31 | 71 | -57 | -32 | normal
2007-11-27 | 140 | sunny | 23.4 | 28.3 |  | 26.3 | 30 | 140 | 134 | 80 | 70 | 60 | 50 | 34 | 79 | -62 | -29 | normal
2007-11-28 | 141 | sunny | 20.5 | 28.8 | 47 | 30.3 | 30 | 145 | 135 | 80 | 70 | 60 | 45 | 21 | 74 | -60 | -29 | normal
2007-11-29 | 142 | sunny | 18.4 | 27 | 50 | 33.5 | 30 | 150 | 140 | 80 | 65 | 60 | 40 | 21 | 68 | -60 | -30 | normal
2007-11-30 | 143 | sunny | 18.4 | 26.2 | 50 | 31.6 | 30 | 150 | 140 | 80 | 65 | 60 | 40 | 23 | 69 | -59 | -30 | Change paper of record machine
2007-12-01 | 144
2007-12-02 | 145
2007-12-03 | 146 | cloudy | 25.2 | 26.5 | 55 | 40.5 | 30 | 150 | 140 | 80 | 70 | 60 | 40 | 15 | 70 | -60 | -32 | Press. of SFU1-1;1-2 are high, of EFU1 is low
2007-12-04 | 147 | sunny | 21.3 | 29.3 | 60 | 37.3 | 30 | 150 | 140 | 80 | 70 | 60 | 40 | 17 | 77 | -60 | -28 | Press. of SFU1-1;1-2 are high, of EFU1 is low
2007-12-05 | 148 | sunny | 21.9 | 29 | 52 | 34.5 | 30 | 150 | 140 | 80 | 70 | 60 | 45 | 25 | 73 | -63 | -29 | Press. of SFU1-1;1-2 are high, of EFU1 is low
2007-12-06 | 149 | sunny | 22 | 29.6 | 50 | 34.5 | 30 | 150 | 140 | 80 | 70 | 60 | 40 | 23 | 69 | -52 | -26 | Press. of SFU1-1;1-2 are high, of EFU1 is low
2007-12-07 | 150
2007-12-08 | 151
2007-12-09 | 152
2007-12-10 | 153 | cloudy | 24.6 | 28.6 | 68 | 50 | 30 | 200 | 190 | 90 | 65 | 60 | 35 | 0 | 62 | -98 | -30 | 9th Dec.07 Electric stopped 4 times from 17h to 21h.
2007-12-11 | 154
2007-12-12 | 155
2007-12-13 | 156
2007-12-14 | 157
2007-12-15 | 158
2007-12-16 | 159
2007-12-17 | 160
2007-12-18 | 161
2007-12-19 | 162
2007-12-20 | 163
2007-12-21 | 164
2007-12-22 | 165
2007-12-23 | 166
2007-12-24 | 167
2007-12-25 | 168
2007-12-26 | 169
2007-12-27 | 170
2007-12-28 | 171
2007-12-29 | 172
2007-12-30 | 173
2007-12-31 | 174
2008-01-01 | 175
2008-01-02 | 176
2008-01-03 | 177
2008-01-04 | 178
2008-01-05 | 179
2008-01-06 | 180

## Trend graph
The Graph of record of dairy checking BSL-3 Mobile Laboratory
(2)Consideration
The case When passage days are given and pressure loss will be expected.
|  |  | Passage days | Pressure loss
|  |  | [days] | [Pa]
|  |  | 180 | #REF!
The case When pressure loss are given and passage days will be expected.
|  |  | Pressure loss | Passage days
|  |  | [Pa] | [days]
|  |  | 80 | #REF!
1. 7/27, no abnormality.
25. 8/20 16h45 decrease the set temperature of PAC form 25 to 23 because to hot
26. 8/21 no abnormality.
27. 8/22 the recorder stop 10 hours, the reason is loss of power
28. 8/23 increase the set temperature of PAC form 23 to 24
29. 8/24 no abnormality.
30. 8/25 Stop the mobilab at 11h20 to repair the electric system of NIHE, 12h20 run the mobilab
31. 8/26 no abnormality.
32. 8/27 no abnormality.
33. 8/28 no abnormality.
34. 8/29 cleanup 2 supply air filter, by ITAGAKI sensei and Dung
35. 8/30 no abnormality.
36. 8/31 no abnormality.
37. 9/1 no abnormality.
38. 9/2 no abnormality.
39. 9/3 no abnormality.
40.9/4 change the ink for the recorder.
| 41. 9/5 no abnormality. | no abnormality.
42. 9/6 no abnormality.
43. 9/7 no abnormality.
44. 9/8 no abnormality.
45. 9/9 no abnormality.
46. 9/10 no abnormality.
47. 9/11 change the set valua of PAC from 24 to 25
48. 9/12 decrease the set valua of PAC from 25 to 24
49. 9/13 no abnormality.
50. 9/14 EF1 has the unusual voice
51. 9/15 no abnormality.
52. 9/16 no abnormality.
53. 9/17 no abnormality.
54. 9/18 Ante Room has unusual water (the reason is the heavy rain last night)
55. 9/19 no abnormality.
56. 9/20 no abnormality.
57. 9/21 no abnormality.
58. 9/22 no abnormality.
58. 9/23 no abnormality.
59. 9/24 degrease the set temperature from 24 to 23 by Dung and Hang
60. 9/25 no abnormality.
61. 9/26 no abnormality.
62. 9/27 no abnormality.
63. 9/28 no abnormality.
64. 9/29 no abnormality.
65. 9/30 no abnormality.
66. 9/31 no abnormality.
67. 10/1 EF1 had sound, it had water around PAC. Increase the set pessure of Lab from -70 to -60
68. 10/2 no abnormality.
69. 10/3 water from outside thought to machine room, pasted silicon by Itagaki sensei and Dung
70. 10/4 water from outside thought to machine room, pasted silicon by Itagaki sensei and Hang
71. 10/5 same 10/4
72. 10/8 there was strange sound in fan system; Itagaki Sensei and Dzung paste silicon on the wall of machine room.
73. 10/9 Miki sensei and Hang, Dzung check supply air volume
74. 10/11 Lab. Room temperature was high
75. 10/12 Lab. Room temperature was high
76. 10/15 Lab. Room temperature was high, had strange sound in fan and PAC
77. 10/16 Lab. Room temperature was high, had strange sound in fan and PAC
78. 10/17 Lab. Room temperature was high, had strange sound in fan and PAC
79. 10/18 Lab. Room temperature was high.
80. 10/19 Lab. Room temperature was high.
81. 10/22 there is sound at upper of PFU0 and fan of PAC hot block
82. 10/23 Mr. Dzung repairs the sound at upper of PFU0
83. 10/24 Decrease PAC set point temperature to 21
84. 10/25 Increase PAC set point temperature to 25
85. 10/29 Metec Comp. check Outside Unit (AHU) and spray water to wash filter; Mr.Itagaki and Ms.Hang measured temp. of Lab : about 24-25 degree.
86. 10/30 PUHV-P224M-E has sounded creakly
87. 11/1 Reseachers said that it was very hot in Lab. -> Ms. Hang measured temp. of Lab 26.4 degree